## Slide 1: Friday 4.5.2012

## Slide 2: Friday
Investigation cold compressor problem sector 81
Access for cryo, experiments (Alfa, Atlas, CMS), check sand level in FTDP19 PM32, BLMD in 4R5, EN/EL visual control of water cooled cables in IP2, IP4, IP6 and IP8, CV for visual inspection of ventilation units in IP2 and IP8
EPC intervention on:
  - RCBV28.L8B1: Problem of the communication; converter to be replaced. - RCBV17.R7B2: Trip the 2012-04-29 00:49 due to internal converter problem; converter to be replaced. - RCO.A67B2 : Trip the 2012-05-02 10:41 due to a power converter problem; converter to be replaced
Knud: Extraction switch of RB.A56 in UA63: Since a few days the breaker A2 has been in open state (not affecting operation). The complete breaker array was opened and reclosed. All breakers, including A2, closed properly. All looks OK now.

## Slide 3: Changes
Horizontal tune B1 & B2 increased by 2e-3 in collision beam process
Joerg rolled back all the H and V cod function to the status before the last TS (~last physics fill)
BLM monitor factor change from 0.1 to 0.2 to accommodate for losses during the squeeze for: BLMEI.06L7.B2I10_TCLA.C6L7.B2 BLMEI.06L7.B2I10_TCLA.D6L7.B2
  The symmetric monitors on the right side had their monitor factors increased from 0.1 to 0.2 already on 13.4.2012
added RCBV17.R7B2 and RCBV28.L8B1 in SECTOR78 and ORBIT_V HWG, removed them from not used

## Slide 4: Saturday
0:00 Cryo conditions OK, starting precycle for the whole machine
Lost Sector 78 due to cold compressor fault
3:13 Access cryo point 8
Plan
Recovery ~21:00 – midnight
Next physics fill with 1380 bunches
Fill with low intensity to do the loss map B1V at collision, high gain orbit feedback in squeeze, and dump with FMCM check RD34 IP7 (set to OFF).