## Slide 1: LHC progress
Week 30 summary 30th July 2012
Coordination: Mike Lamont & Bernard Holzer

## Slide 2: Overview

## Slide 3: Week 30
Fill | End | Stable | Peak | Int fb-1 | Dump
2872 | Mon 10:20 | 15h5m | 5.58 | 166 | OP
2873 | Tues 10:15 | 12h0m | 5.83 | 151 | OP
2875 | Wed 09:10 | 15h24m | 5.72 | 172 | OP
2880 | Thu 13:21 | 9h17m | 5.49 | 118 | Triplet R1 – QPS SEU (tbc)
2882 | Thu 21:50 | 30m | 5.7 | 9 | Trip of LHC dipole
2883 | Fri 01:50 | 4m | 2.6 | 0.3 | Beam loss B1
2884 | Fri 14:11 | 9h40m | 5.42 | 119 | OP
2886 | Sat 03:00 | 3h43m | 5.65 | 61 | Collimation communication
2887 | Sat 10:30 | 4h47m | 5.88 | 76 | Network controller – point 5 collimators – access system
2888 | Sun 08:30 | 15h48m | 6.08 | 182 | OP
2891 | Mon 00:23 | 6h9m | 6.13 | 98 | Spurious switch opening RQF.A12
2892 | Ongoing |  | 6.17 |  | 

## Slide 4: Luminosity

## Slide 7: Brightness

## Slide 8: Timeouts
Monday | 11:15 Access for fire brigade ... electrical problem in water cooling pump 18:40 restart
Tuesday | ADT gain calibration at 450 GeV
Wednesday | AM Morning: switch LHCb polarity and test ramp 14:00 access - various 16:00 restart, precycle ... trip of RQ10.R8 (converter fault) Restart 20:25
Thursday | Access for cryogenics valve at D4L5 on the DSL line for the main circuits of S45 (in shadow of triplet recovery) Injection optimization by Chiara and Wolfgang
Friday | 15:30 h=9 low emittance beam test 16:00 beam dump due to open access door 20:00 controls problem in PS 21:00 back to standard physics fill
Saturday | 10:06 beam dump: loss of network communication, access needed to reset switch 15:20 injection for physics
Sunday | Test ramps for chromaticity

## Slide 9: Instabilities, beam loss etc.

## Slide 10: 2883 – early Friday morning
Activity kicks off on beam 1 – end of squeeze
Sustained beam loss both beams – finally dumping on collimator temperature interlock
QH B1 low – on or near 100 Hz
Tune Shift
100 Hz
100 Hz

## Slide 11: Associated beam size increase
Federico Roncarolo

## Slide 12: 2859 – end squeeze
Stepping back a little over a week…

## Slide 13: 2860 – collision beam process
Instability B1H – losses on B2
Faster (~ 25 s)

## Slide 14: 2862 – collision beam process
Similar…
Instability B2H & B1H
Haven’t seen this since

## Slide 15: 2866 – B2H end squeeze
100 Hz

## Slide 16: 2867 – B2H end squeeze
100 Hz
Now taking a lot of care not to put the tune on 0.3068 (3450 Hz)

## Slide 17: Tunes@ injection&ramp
0.28 = 3149 Hz
Up to now take a lot of care to keep horizontal tunes on this value (QFB)
Yesterday moved QHB2 to 0.282 at injection & ramp…
Sample size = 2:
  Reduced losses at end ramp (perhaps)
  Not reflected in BSRT fast scan…

## Slide 18: 2891 – end ramp

## Slide 19: BSRT beam 1

## Slide 20: BSRT Beam 2

## Slide 21: Beam sizes before/after TS
Federico Roncarolo
B2 H and V seems to have changed, even though the BSRT meas. are biased by a larger noise

## Slide 22: 50 Hz
Not instrumentation – not there without beam – seen in all 3 BBQ
Horizontal plane – both beams
Limited number of sources – narrow line, no sidebands
Probably dipole field, don’t see it on the tune…

## Slide 23
RB.A34
ALICE SOLENOID
Plus a few others

## Slide 24: Summary
Ramp, squeeze and collide looking smoother
  As always if there are losses, it’s B2
Usual lifetime dip at the moment of collisions
  B2 down to 1 hour, 5-6% beam loss – tunes?
Emittances from luminosity look a little large
  B2 between 450 GeV and collisions?
Chromaticity measurement to be analyzed

## Slide 25: Q’H B1

## Slide 26: Changes
Longitudinal blow-up
  Programmed bunch length increased from 1.2 to 1.3 ns
Transverse feedback
  Gain calibration
  B2H gain reduced during squeeze by 25%
Injection and ramp B2H tune to 0.282
LHCb polarity
Injection sequence modification for Alice

## Slide 27: OF NOTE

## Slide 28: Summary of the ADT Gain renormalization
The calibration constants which were used in the system until today date from 2010. As the tetrodes in the power amplifiers are ageing and being replaced, and the Beam Position Readings change with the beam intensity settings variations have occurred since.
Since the last technical stop in June 2012 all power systems are populated with new tubes and back to nominal power gain.
From the measurements we have programmed new calibration factors today:
  HB1 old 9213 new 10000
  VB1 old 8804 new 9199
  HB2 old 11466 new 7942
  VB2 old 6197 new 5167
The effective gain of the Horizontal Beam 2 system was therefore lowered by 31% and it should be now consistent again with the "normalized gain" knob.
Wolfgang Hofle, Daniel Valuch

## Slide 29: RF phase noise – CCC diagnostic
Thanks to Fabian Follin, Michael Jaussi, Themistoklis Mastoridis
Plus accompanying tutorial

## Slide 30: 32 bunch h=9 test
Attempt dogged by unrelated problems
But previous emittances of 1 micron with 1.2e11 ppb on flat top of SPS could not be re-established
Indications that problem also effects nominal 50 ns beam
PS/TT10 matching a suspect (Karel)
Might also been there already at injection in PS
Could explain decreased brightness

## Slide 31: Incoming
Gianluigi & Barbara
VIP this afternoon – dump beams ~14:30..
Octupoles…
h=9

## Slide 33: In our midst…
We have a multi-talented, intelligent, good natured, humble, hard working physicist.
Over the years he has made a profound contribution to the success of the LHC and many other projects.
He has nurtured a generation of students, fellows and young physicists with good humour and empathy.
As a founding member of the LHC coordination team he’s been in the thick of over the last few years and it’s been a real pleasure working with him..

## Slide 34: This man is…