## Slide 1: UTC-Timing problem
P.Charrue for the BE/CO/Timing team

## Slide 2: Observations
Starting last Wednesday at 20:49:14
  UTC timestamps of some systems was observed to be wrong
Impact of this problem
  Logging and post mortem data are tagged with wrong UTC time
Normal events and SMP data were correctly distributed (Ruediger)

## Slide 3: What is the problem
Every 1ms: 8 events are sent on the timing network
Every 100ms: the SMP system sends few events to central timing to be distributed
Every 1s: the UTC event is sent on the timing network
The problem is a result of two issues:
Central Timing priorities configuration
Bug in the Timing Receiver Cards firmware
Central Timing priorities configuration
The central timing firmware is configured with the following priorities:
  1st => events
  2nd => SMP, asynchronous events
  3rd => UTC
When the SMP events distribution coincides with the UTC-second frame distribution, the central timing does not send the UTC frame in favor of the SMP events
Bug in the Timing Receiver Cards (CTR) firmware
A bug in the CTR firmware was discovered in 2010 that, when the UTC frame does not arrive, the CTR substitutes it with an older frame resulting in a wrong UTC time
  A new corrected CTR firmware is available since January
  EPC already upgraded and experienced NO problem last night

## Slide 4: Progress Report
The timing team managed to reproduce the problem in their lab
A new version of the central timing firmware is ready
  The priority of the UTC slot is increased
  Asynchronous events will not preempt the distribution of UTC
The new firmware is tested in the timing lab and the UTC problem did not appear
The new firmware has been deployed on the BE/CO testbed and after 16 hours of intense events distribution tests, no problem was observed

## Slide 5: Actions
Central Timing Server
Today at 9h00 the new firmware will be deployed on the operational central timing master server (A)
  The slave (B) server will remain with the previous version
  The timing team will be in the CCC to monitor the events
A ramp of low intensity (3 bunches?) will be done to check if all is working ok
A decision to declare the new firmware operational will be taken by the EIC and the timing experts
Timing Receiver Cards
CO will coordinate the upgrade of the CTR firmware with the remaining equipment groups which did not take the new version in January (~200 CTRs)
  Firmware upgrade takes a few minutes and can be done remotely
Reminder
The timing system is designed without safety-critical applications in mind and event losses is possible to occur under certain conditions
Critical or protection functionality should NOT rely on the timing system