## Slide 1
Distribution network fault on LHC1
10/07/2011
F Duval, G Cumer on behalf of EN/EL 10/07/11

## Slide 2
1) FACTS

## Slide 3
3 major events in 30 min (11:03, 11:11, 11:34)
  Discrimination not easy but last was worst (short on Verbois OHL)
  Impact on several points (starting contact: EHT2 pulsed, Diesel network, Meyrin admin. loop)
  False intertrip on MP7 (second in a row after 3 month of storms)
  Autotransfer failed to refeed SEM12 (Io on couplers)
1) FACTS

## Slide 4
1) FACTS

## Slide 5
Situation after autotransfert 11:34:48
  All machines off
  LHC loop and ATLAS partially off
  MEYRIN reenergized from Swiss network
  DIESEL generators started well on all LHC points
Situation after Piquet reconfiguration 13:50
  Piquet at work at 12:15 (difficult to understand)
  fail to refeed loop from LHC2 ( Io) at 12:58
  LHC loop fed from LHC2 (in two steps) 13:28
  ATLAS fully refed at 13:49
Network back to the standard configuration at 16:00
1) FACTS

## Slide 6
1) FACTS

## Slide 7
2) ANALYSIS
Another false intertrip on MP7
  second in a row after 3 months of storm seasons
  intertrip will be deactivated ASAP
  Fiber optics will be installed for intertrips
Io twice attempting to reenergized SEM12 (LHC loop + ATLAS)
  No explanation yet
Unexpected and complex situation for Standby service
  2h15 before renergizing LHC1 (too long)