## Slide 1: Summary of week 19
Machine Coordinators: G. Arduini, M. Lamont Main aim: Luminosity production

## Slide 2: Week 19
Mix of performance and machine availability issues
Cryo. Pt. 8
1092
480
1380

## Slide 3: Last 24 hours
04:25 Stable beam #2623 1.23e11 ppb, 4.13e33 cm-2s-1.
08:15 cold compressor off in point 2...(Cooling problem)
09:50 Beam dumped by operations - cryogenics recovery
15:00 Cryo back, pre-cycle etc.
18:54 Stable beams #2624. 1.28e11 ppb, 4.34e33 cm-2s-1
00:03 UFO at BLMQI.06R8.B2E10_MQML. Beam dump
Re-steering required for TI2
03:28 STABLE BEAMS #2627. 1.27e11 ppb, 4.11e33 cm-2s-1

## Slide 4: Fills of the week
Fill | Day | Nb | L (h) | Int L (pb-1) | Dump
2593 | Mon | 1092 | 4.6 | 41.1 | Electrical network, FMCM
2596 | Mon | 1092 | 10.6 | 91.8 | OP
2605 | Th | 480 | 1.3 | 5.5 | End of fill test
2608 | Th | 1380 | 0.5 | 6.8 | UFO
2609 | Th | 1380 | 4.5 | 44.5 | ADT vac. Gauge trip
2616 | Fr | 1380 | 1.9 | 26.0 | Vacuum crate PS failure
2617 | Fr | 1380 | 0.4 | 5.9 | Q7.R1 trip (SEU?)
2621 | Sat | 1380 | 13.3 | 120.5 | OP
2623 | Sun | 1380 | 5.4 | 62.3 | Cryo pt. 2
2624 | Sun | 1380 | 5.2 | 63.3 | UFO
2627 | Mon | 1380 | 4.5 | ~55 | 
 |  |  | 52.2 | 523 | 
Stable beams ~ 52.5 hours in total (31.1 %)

## Slide 5: Integrals

## Slide 6: Main faults
Cryo Pt8
 | Hours | Faults
Mon 7.5 | 3 | Injectors, RF control, BPM LSS6
Tue 8.5 | 8 | Injectors, RQTL11.L5B1 (PC), Cryo Point 8
Wed 9.5 | 24 | Cryo point 8/Electrical problem in P1 (18kV/400 V transformer)/ALICE dipole/RF controls
Thu 10.5 | 4.5 | RF controls, BLMs controls, Injection
Fri 11.5 | 15 | RF controls, injection, Vacuum crate failure , QPS connector
Sat 12.5 | 7.5 | Recovery from Fast abort sector 12 (dump resistor cooling), access for RCBCV9.L5B1 repair, injection losses due to different cycle in the SPS
Sun 13.5 | 5.5 | Cryo compressor point 2 – Cooling water problem
~ 67.5 hours in total (40 %)

## Slide 7: Losses at the end of the ramp and squeeze (B2)
Deterioration started already before technical stop and continued after technical stop. Effects visible already during the ramp
Fill 2536 – Before technical stop
Fill 2538 – Before technical stop (dump during ramp - HV)
Fill 2589 – After technical stop

## Slide 8: Orbit and losses in the squeeze
B2: Losses and H TCP orbit well correlated. Less evident for V-plane
J. Wenninger

## Slide 9: Orbit FF – squeeze – beam 2
Sigma H at TCP ~300 microns
TCP ~5.1 sigma
R. Steinhagen, J. Wenninger
60% correction applied

## Slide 10: High gain OFB test
Blue : before high BW, Magenta: OFB BW x10, Black: after 100% FF
B1H
B1V
B2V
B2H
J. Wenninger

## Slide 11: Losses in squeeze at TCP
Improved but still spikey

## Slide 12: Losses during ramp and squeeze
Increased losses on Beam 2 observed already before TS
Worse after technical stop:
  Related to larger tails and larger emittance at higher energy
  Mostly appearing between 2.5 and 2 m
  Correlated with (small) orbit distortions at TCPs and (small) relative offsets beam/collimator centre adding up for B2 in particular
  Losses enhanced by reduced gain of the transverse feedback on 12 bunches
Actions:
    Verifications in the injector chain
    Transverse damper modulation off
    Collimator set-up at top energy checked
    BLM thresholds increase + review of the thresholds (rMPP/LMC)
    OFB higher bandwidth in squeeze and feed-forwarded
    Investigations on the optics and collective effects expected during the squeeze from 2.5 to 2 m  LMC
    Scraping of tails at low energy  to be done

## Slide 13: Instability – B1 H
Occurring when CMS in collision and ATLAS not yet fully head-on. Lifetime good up to that point.

## Slide 14: Instability
Instability at the end of the collision process (separation bumps collapsed). Residual separation of ~2.1 s in IP1 and ~1.2 s in IP5 and 3.2 s in IP8 (estimated from luminosities at the moment of the dump). The separation in IP1 and 5 is likely the effect of the orbit correction during the squeeze.
LCMS
LATLAS
B1H osc. Ampl.
LLHCb

## Slide 15: Instability Damper pick-up signals
Thanks to W. Höfle!!

## Slide 16: Actions
Went back to low number of bunches but with 50 ns spacing to get as much as possible same orbit
Luminosity scan to determine collision offsets and correct them  incorporated for next fill
Analysis of data ongoing
IP1 - H
IP5 - V
IP5 - H

## Slide 17: Instability
5 microns
~1.7 sigma
~1.5 sigma

## Slide 18: Status
Losses:
  Still losses during the ramp (not negligible)
  Reduced during the squeeze (particularly between 2.5 and 2 m and more recently at ~1.5 m) although spikey.
  Warning levels reached:
    at the end of the ramp (TCSG/TCLA in point 7: 80 s running sum to 50 % of threshold)
    During the squeeze between b*= 2.5 and 2 m and at 1.6 m (TCSG/TCLA in point 7: 1.3 s running sum to 56% of threshold)
Instability: can be controlled by the transverse feedback provided small offsets (< 1 s) at the end of the collision process.

## Slide 19: Performance
Loss of brightness ~20% during technical stop  checking LHC and injectors. Eemittance comparison through the chain to understand the origin. Concentrating particularly between PS and SPS.
Need chirp to measure the tune during the ramp

## Slide 20: Performance
c/o ATLAS
Fill 2536 – Before technical stop
Fill 2624 – Now

## Slide 21: Pending
Beam quality from the injectors
Injection delicate: heavily relies on quality of the beam form SPS. Collimator aperture opened form 4.5 to 5 s in both injection lines.
Orbit in collision needs to be corrected and trims incorporated (in particular point 5)
TDI jaw deformation  check to be done after long high intensity fill