## Slide 1: Sat 13/08 – Sun 14/08
02:45 Trip of cold compressor in point 8
Cause: sudden variation in the measured value of the rotation speed of the turbine (SEU or failure of the control card) on magnetic bearings leading to a fast stop of the compressor
Morning: diagnosis and attempts to restart the compressor
14:30 intervention of the cryo controls team to recalibrate the parameters controlling the rotation and axis of the turbine
17:30 Compressor restarted
00:24 Trip of the compressor (this seems to point to an issue with the controls card more than SEU)

## Slide 2: Plans
Experts contacted to see what are the next steps (electronics replacement?, compressor replacement?). Access required likely.
For sure no beam before Tuesday
Access request from ATLAS (10 AM)
Measurements in the transfer lines (new optics in TI2)